## Slide 1
CCGT Piping
Construction Guide
Summary of the CCPP Piping Guide Book, from utility systems to COD
Piping Construction Department
Notes: Summary deck based on the CCGT Piping Guide Book (58 pages).

## Slide 2
Guide at a glance
CCGT Piping Guide | Summary
2
A practical reference for combined cycle power plant piping construction.
Prioritize safety and quality at every stage, from material receipt to turnover.
Content may change with the project specification, application code, and design criteria.
1
Purpose
Practical reference for CCGT piping construction
2
Piping Construction in a CCPP Project
Systems and installation routes: utility, simple cycle, combined cycle
3
CCPP Key Milestone
Piping prerequisites for each commissioning step
4
Piping Construction Management
Planning, materials, U/G and A/G piping, steam piping, supports, testing
5
Lessons Learned
Nine field cases with root causes and preventive measures

## Slide 3
Piping work follows the plant build-up sequence
Utility supply first, then Simple Cycle (GT), then Combined Cycle
CCGT Piping Guide | Summary
3
1 Utility Systems
Fire water, potable and service water
Demineralized water
IA, SA and N2
Vents, drains, waste water
Basis for cleaning, hydro test and flushing
2 Simple Cycle (GT)
GT and ancillary systems
Fuel gas and fuel oil supply
Lube oil and cooling (CCW)
GT air intake and exhaust
Enables GT start-up
3 Combined Cycle
HRSG HP / IP / LP, HRH, CRH steam
Feed water and condensate
Sampling
Chemical dosing
Water-steam cycle
4 STG & Condenser
STG steam
Bypass steam
Steam drain
Circulation water (CW)
Steam turbine and heat rejection
Utility systems are installed early because they supply water, air and fire protection for construction and testing.

## Slide 4
Water-steam cycle: what the piping connects
Condensate and feed water path (top) and steam path (bottom)
CCGT Piping Guide | Summary
4
Condenser hot well
Condensate pumps (CEP)
Preheater (CPH) or LP economizer
Deaerator or LP drum
Boiler feed pumps (BFP)
HP / IP economizers
HP / IP / LP drums, evaporators
Superheaters
HP turbine
Cold reheat (CRH), reheater
Hot reheat (HRH)
IP / LP turbine, condenser
Water quality
Sampling lines from HRSG to sampling rack
Chemical dosing points on feed water and steam
Steam quality
Drains and vents at low and high points
Continuous slope toward drains, traps at low points
Turbine protection
Bypass: HP to CRH, HRH and LP to condenser
Stop and control valves, gland and seal steam

## Slide 5
STG and condenser systems: key installation points
CCGT Piping Guide | Summary
5
1
STG steam
HRSG outlet headers, then stop and control valves, then turbine casing
Hangers and spring supports absorb thermal expansion
Precise alignment avoids stress on turbine nozzles
2
Bypass steam
HP bypass goes to the CRH line; HRH and LP bypass go to the condenser
Stop and control valves, relief devices, drains, vents
Protects turbine during start-up, shutdown and load changes
3
Steam drain
Drains at low points, bends and equipment inlets
Steam traps separate condensate; vents release gases
Continuous slope, drain always below the header
4
Circulation water (CW)
Large-bore GRP underground, rubber-lined carbon steel above ground
Heavy pipe needs robust supports; alignment is critical
Expansion joints secured with tie-rods

## Slide 6
Key milestones and the piping behind them
14 steps from utility supply to commercial operation
CCGT Piping Guide | Summary
6
1
Utility Systems
2
Power Receiving
3
Demi Water Production
4
Cooling Water Load Test
5
HRSG Hydro Test, Pump Load Test, Chemical Cleaning
6
GT Lube Oil Flushing and Functional Test
7
GT Initial Firing
8
GT Synchronization
9
Steam Blowing
10
ST Lube Oil Flushing
11
ST Steam Admission
12
ST Synchronization
13
Performance and Reliability Tests
14
Commercial Operation Date (COD)
Water, cooling and cycle readiness
GT operation
Steam cycle
Performance and handover

## Slide 7
Piping that must be ready before each step
CCGT Piping Guide | Summary
7
Commissioning step | Piping prerequisite
Power receiving | Fire water and potable water (WT/WWT, CEB) done; IA piping tested and purged
Demi water | Piping from WT building to demi tank, pumps and HRSG installed, supported, hydro-tested
HRSG hydro and chemical cleaning | HRSG steam, feed water and condensate piping; BFP installed; temporary loops, blinds, vents, drains
GT lube oil flushing and firing | Fuel line cleaned and N2-purged; CCW and IA lines complete; lube oil piping tested; exhaust supported
Steam blowing | Steam and bypass piping hydro-tested (at least 3 months before) and insulated; temporary piping and silencers
ST steam admission | HP / IP / LP steam, drains, vents, seal steam, sampling and dosing lines; support TA on site
Performance and reliability tests | All permanent piping complete; test boundary valves tight; measurement points calibrated
COD | Punch list and NCRs closed; insulation, labeling and support corrections finished

## Slide 8
Piping construction management: six control areas
CCGT Piping Guide | Summary
8
1
General management
Review contract and ASME B31.1 before work
WPS / PQR / WQT for every weld; P91, P22, P11 critical
NDE and PWHT as specified
2
Drawing control
Coordinate with engineering on latest revisions
Install only per approved drawings and changes
3
Material control
Real-time issue and inventory tracking
Early order: alloy pipe, electrodes, WQT coupons
Store tagged spring supports and snubbers separately
4
Manpower
Dedicated scaffolding team
Support team from the start of piping erection
Experienced foremen for steam supports
5
System-based priority
Utilities first, then headers on pipe racks
Bulk large-bore lines, finish system by system
Follow commissioning schedule
6
Hydro test and isolation
Complete hydro tests before commissioning
Isolation valves upstream of each building if tests come later
Plan vents and drains, keep valves accessible

## Slide 9
Underground piping by material
CCGT Piping Guide | Summary
9
HDPE
Fire, potable and service water
Butt fusion or electrofusion; log fusion parameters
Anchor blocks at bends, tees, valves
NFPA / AWWA, or FM / UL approved
GRP
Circulating water, chemical service
Uniform bedding to avoid point loads
Thrust blocks at direction changes
Check U/G to A/G alignment before connection
CPVC
Chemical service water
Solvent-welded at ambient temperature
Avoid sharp bends; allow for expansion
Hydro test before backfill
PE-coated steel
High-pressure water, fuel, process
Field joint coating and holiday test
Cathodic protection as needed
Protect coating during backfill
Sequence: trench and bedding, lower pipe, joint, inspect, hydro test, layered backfill, as-built survey.
If a U/G line meets A/G piping without an isolation valve, the A/G pressure test includes the U/G section.
Early U/G lines need protection (sand bedding, cover boards); confirm tank erection dates first.

## Slide 10
Aboveground piping: process and material controls
CCGT Piping Guide | Summary
10
Spool inspection
Erect and align
Weld and NDE
Pressure test
Insulate and paint
As-built and turnover
Material | Key controls
Alloy steel (P91, P22, P11) | Heat number check; preheat and interpass control; PWHT with calibrated equipment; expansion loops, guides, anchors; controlled heat-up
Carbon steel | Soft slings; guides, shoes and anchors first; adjust supports for slope; dry, primer and paint after test
Stainless steel | Non-ferrous handling and wooden storage; low heat input; pickling and passivation; chloride-free test water
Galvanized / coated | Padded slings and liners; minimize welding; recoat field welds immediately; repair coating damage

## Slide 11
Steam piping and supports
CCGT Piping Guide | Summary
11
Steam piping rules
Follow ASME B31.1, stress analysis and traceability records
Erect from the turbine nozzle outward; avoid cold pull at turbine
Check slope and tolerances at turbine and HRSG connections
Preheat, interpass control and PWHT for P91, P22, P11
Hydro test before insulation; dry and preserve after test
Steam piping supports are the hardest installation task
1
Rigid
Anchors and guides; transfer static and dynamic loads
2
Spring
Set to cold load; keep travel stops until hydro test ends
3
Snubber
Restrain shock loads, allow slow movement; function test
4
Sliding
Axial movement with lateral restraint; check clearance
5
Special
Sway braces, struts, sliding shoes for wind and vibration
Support TA: verifies cold setting after hydro test and thermal movement at steam admission (hot function).

## Slide 12
Pressure test: ASME B31.1 and B31.3
Each test package names the governing code, pressure, hold time and medium
CCGT Piping Guide | Summary
12
Item | ASME B31.1 (Power Piping) | ASME B31.3 (Process Piping)
Applies to | Steam, feed water, condensate, drains; boiler external piping | Systems designated by the spec: fuel gas, fuel oil treatment, chemical dosing
Hydrostatic pressure | At least 1.5 x design pressure | At least 1.5 x design pressure, corrected by ST/S (max 6.5)
Hold time | At least 10 minutes | At least 10 minutes
Pneumatic pressure | 1.2 to 1.5 x design pressure | 1.1 x design pressure
Pneumatic procedure | Stepwise: check at the lesser of half test pressure or 170 kPa, then reduce to design pressure for leak exam | Same stepwise method
Other tests | Initial service leak test not allowed for boiler external piping | Sensitive leak test if specified; initial service test only for Category D
Hydro is preferred; pneumatic only with risk assessment and relief devices. Project specification and Owner PO take precedence; verify the code edition.

## Slide 13
Other field practices
CCGT Piping Guide | Summary
13
1
Control valve
Before hydro test: remove internal parts and actuator, fit blind flange on valve body top
After test: reinstall under the supplier TA witness
Align hydro schedule with the TA visit
2
Check valve
Install in arrow direction, orientation per manufacturer
Remove or gag internals for hydro; restore afterwards
Protect internals during flushing, cleaning and steam blowing
3
Pump piping
Keep straight run upstream of the suction nozzle (about 5D)
Comply with spacing and vendor requirements
4
Instrument connections
Review hook-up drawings
Steam: side taps, sloped impulse lines with condensate pots
Liquid: side or slightly below centerline; gas and air: top

## Slide 14
Lessons learned: nine field cases
CCGT Piping Guide | Summary
14
Case | Root cause | Prevention
HP steam supports rub in HP turbine | Expansion constrained at HP MSV connection | Erect from turbine outward; follow drawings and cold setting
Steam piping slope | Reverse slope; fit-up did not check slope | Verify slope against drawings before final weld-up
Steam supports installed wrongly | Hasty work, weak drawing understanding | Experienced crews; enough time; inspect cold setting and gaps
DN900 butterfly valve reversed | ISO flow marking conflicted with design intent | Check ISO against P&ID before installation
Missing expansion joint tie-rods | Tie-rods omitted; buried GRP moved | Install complete tie-rod assemblies
Steam drain too high | Design error, drain above flash tank | Design review: drain below header
Sampling line blocked, tie-in mismatch | Routing not verified; plastic caps left on | 3D model review; end-cap and cleanliness checks
GT fuel oil filter omitted | Design oversight, supplier scope gap | Confirm GT fuel requirements before construction
CCW branch without isolation valves | Design used operating criteria only | Add branch isolation valves; plan for construction sequence

## Slide 15
Key takeaways
1
Plan piping around commissioning milestones, utilities first.
2
Finish hydro tests before commissioning; isolate for later work.
3
Control supports: install per drawing, verify cold setting with the TA.
4
Check slope, flow direction and elevation on drawings before fit-up.
5
Keep lines clean: remove caps, flush, purge and preserve.